## Report
Doc No: |  | 9823-PW-QAT-ITC-0009 |  | PIPE LAYING INSPECTION FIELD RECORD ITR-PLA-001
Effective Date: |  | 2025-07-08
Revision No: |  | 1
Page No: |  | 1 of 1
PROJECT INFORMATION
PROJECT NAME: |  |  | ALKIMOS DN1600 TRUNKMAIN |  |  |  | PROJECT NUMBER: |  | C1/1000004254
SECTION-SUBLOT: | [6 empty] | ITP:
PIPE RECORDS
Pipe/ Fitting Details | [6 empty] | PIPE SPECIFICS |  |  | FINAL CHECK |  | APA Signoff
Date Installed | Pipe Chainage | Pipe No Stamp or Fitting ID | Joint Type (WR, RRJ, WB, or CWB) | Pipe Installed to Wittness Mark (Y/N) | Internal Rubber Seal Check (Y/N) | Alignment & Deflection Check Alignment: Hor ±100mm/ Vert ±50mm Joint Deflection: see note below | CP Lugs Installed @ 12 O'clock (RRJ ONLY) | Ovality Check ** | Joint Air Test RRJ-WR ONLY (80kPa hold for 2 min) | Internal Cement Liner (OK/Patch) | Spark Testing (OK/Patched)
[12 empty] | NAME | SIGNATURE
|  | * |  | * |  | *** | * | ** | * | *(If Patched) | * (If Patched)
2026-02-12 | 2841.86 | 000615-000550 | RRJ | Y | Y | V: -22mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-12 | 2829.66 | 000615-000248 | RRJ | Y | Y | V: -9mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-12 | 2817.46 | 000615-000276 | RRJ | Y | Y | V: +3mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-13 | 2805.26 | 000615-000288 | RRJ | Y | Y | V: +6mm / H: L0mm | Y | PASS |  | Y | PASS | F. Ronco
2026-02-13 | 2793.06 | 000615-000274 | RRJ | Y | Y | V: -13mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-13 | 2780.86 | 000615-000283 | RRJ | Y | Y | V: +12mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-13 | 2768.66 | 000615-000277 | RRJ | Y | Y | V: -3mm / H: R15mm | Y | Y |  | Y | Y | F. Ronco
2026-02-13 | 2756.46 | 000615-000272 | RRJ | Y | Y | V: -16mm / H: L10mm | Y | Y |  | Y | Y | F. Ronco
2026-02-16 | 2744.26 | 000615-000269 | RRJ | Y | Y | V: +8mm / H: L5mm | Y | PASS |  | Y | PASS | F. Ronco
NOTE: * Has photo requirements. NOTE:** Measurements for Ovality check are to be done at evenly spaced intervals approximately 2Pi/3 around the inside of the pipe NOTE: *** Max deviation and deflection in WR joint is 1.1deg. Max Deflection in RRJ is 0.6deg. Max Deflection with Site Weld Band is 6 deg. No reverse grade permitted- Any exceedance in alignment to be RFI'd.